|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Extinguisher Type** | **Inspection** | **Maintenance** | **Recharging** | **Hydrostatic Testing** |
| Dry Chemical (Stored Pressure) | Dry Chemical (Stored | 1 Year | Empty and Internally Inspect @ 6 Years | 12 Years |
| Dry Chemical (Stainless Steel) | 30 Days | 1 Year | 5 Years | 5 Years |
| Dry Chemical (Cartridge) | 30 Days | 1 Year | Empty and Internally Inspect @ 6 Years | 12 Years |
| Carbon Dioxide | 30 Days | 1 Year | 5 Years | 5 Years |
| Water (Stored Pressure) | 30 Days | 1 Year | 1 Year | 5 Years |
| Wet Chemical | 30 Days | 1 Year | 5 Years | 5 Years |
| AFFF (Liquid Charge Type) | 30 Days | 1 Year | 3 Years | 5 Years |
| FFFP (Liquid Charge Type) | 30 Days | 1 Year | 3 Years | 5 Years |
| Dry Powder | 30 Days | 1 Year | Empty and Internally Inspect @ 6 Years | 12 Years |
| Halogenated (Halon) | 30 Days | 1 Year | Empty and Internally Inspect @ 6 Years | 12 Years |